# ELECTRIC LOCKING SYSTEM EQUIPMENT

# 1	GENERAL

## 1.1	QUALIFICATIONS

The Electric Locking Systems (ELS) as specified this section is based on products manufactured by:

Dortronics Systems, Inc.

1668 Sag Harbor Turnpike

Sag Harbor, NY  11963

Tel:	(800) 906-0137

(631) 725-0505

Fax:	(631) 725-8148

Web:	www.dortronics.com

The Electric Locking Systems Contractor shall base his bid on the system hardware as specified herein.

Delete sections below if alternate products are not acceptable on this project.

Alternate techniques, modifications, or changes to any aspect of these specifications shall be submitted as a voluntary alternate.

Voluntary alternates shall be fully documented and submitted to the Owner or Owner’s representative, at least ten (10) working days prior to bid

## 1.3	RELATED SECTIONS

- Section 08110 - Steel Doors and Frames.

- Section 08210 - Wood Doors.

- Section 08300 - Special Doors.

- Section 08400 - Entrances and Storefronts.

- Section 08710 - Finish Hardware.

- Section 16000 - Special Security Control Equipment.

## 1.4	REFERENCES

Delete references from the list below that are not actually required by the text of the edited section.

- ANSI/DHI A115 Series - American National Standard Specifications for Steel Door and Frame Preparation for Hardware.

- BHMA A156.2 - American National Standard for Bored and Pre-assembled Locks and Latches.

- BHMA A156.13 - American National Standard for Mortise Locks & Latches; Builders Hardware manufacturers Association.

- BHMA A156.18 - American National Standard for Materials and Finishes.

- Certification Listings:

- Underwriters Laboratories, Inc.

- NFPA 101

- FF-H-106C - Hardware, Builders', Locks and Door Trim, General Specification for.

- The Americans with Disabilities Act of 1992.

## 1.5	SUBMITTALS

Delete any of the following paragraphs not required.

- Submit under provisions of Section 01300.

- Product Data:

- Provide manufacturer's standard details and catalog data demonstrating compliance with referenced standards.

- Provide installation instructions.

- Hardware Schedules: Submit a schedule of products specified in this section coordinated with doors and hardware specified elsewhere.

- Samples:  Submit 1 of each type of electromagnetic lock and accessory device.  The Architect for installation will return approved samples on the final openings of the Project.

- Contract Close-out Submittals:

- As built schedule of locks and accessory devices.

- Operation and maintenance materials.

## 1.6	DELIVERY, STORAGE, AND HANDLING

Store products indoors in a secured area, and protect from moisture, construction traffic, and damage.

## 1.7	SYSTEM WARRANTIES

All electromagnetic locks shall be guaranteed against defects in material and workmanship with a lifetime warranty after date of manufacture.  All other components of the Electric Locking System shall be similarly warranted for a period of one year.  Expressed warranties are conditionally based on the requirement that the items covered within the guarantee are used and maintained in accordance with the manufacturer’s recommendations.

# PART 2	PRODUCTS

## 2.1	MANUFACTURER

Provide products by Dortronics Systems, Inc.; 1668 Sag Harbor Turnpike, Sag Harbor, NY  11963.  Telephone:  (800) 906-0137 or (631) 725-0505.  Fax:  (631) 725-4234.

2.3	POWER SUPPLIES / CONTROLLERS

- Provide EDR-System 101 Delayed Egress Controllers as scheduled with locks and accessories as described below:

Edit, or include schedule showing required locations.

- The delayed egress control system shall comply with NFPA Life Safety Code 101.

- When the system is armed and a pressure of no more than 15 pounds is applied to the releasing device for no more than 3 seconds, the lock shall release within 15 seconds.

- The initiation of the release process shall activate the sounder on the console panel located in the vicinity of the door.

- Once the door has been released by an attempted exit sequence, the door shall remain unlocked until manually reset through the keypad, (see #7600 Annunciator / Controller).

- #EDR 101-P Delayed Egress System consisting of a 3 gang console panel with a programming keypad, two status LEDs, an audible alert and a plug-in 9 volt power supply.

- The EDR 101 controller shall be field programmable with the capability of:

- Unique arm and disarm time periods for each day of the week including weekends.

- A master PIN for programming and a secondary PIN to allow alarm by-pass and door unlock for an authorized ingress or egress.

- Reporting of alarm disarm and door unlock to a remote security console (see #7600 Annunciator / Controller).

- Each EDR 101 controlled exit shall also have the following (for each door leaf):

- #xDPS a dedicated door position switch.

- #1110 (1200 lb.) electromagnetic lock.

- #6410-S15 exit bar with one integral SPDT switch (use #6410-S25 exit bar with two redundant switches where required by code).

- #6220 armored flexible door cord.

- Each “delayed egress” scheduled exit door having manual exit hardware devices shall have (for each door leaf) a #1110xSxDPS electromagnetic lock incorporating a built-in attempted egress switch and door position switch

- Each scheduled delayed egress exit shall have a #7101 Auxiliary Keypad mounted on the interior side of each scheduled door for use by authorized persons for passage into or out of the secured areas.

- Each scheduled delayed egress exit shall have a #WR8112 Auxiliary Weather Resistant Keypad mounted on the exterior side of each scheduled door for use by authorized persons for passage into or out of the secured areas.

- Each scheduled delayed egress exit shall have a #5241-24x2LED Key Switch with two status LEDs on a single gang plate mounted on each scheduled door for use by authorized persons for passage into the secured areas.

# PART 3	EXECUTION

## 3.1	INSPECTION AND APPROVAL

Upon successful completion of Electric Locking System installation, the Owner’s authorized representative shall inspect and approve the satisfactory operation of the ELS and related accessories.  Upon receipt of a detailed system adjustment list from the Owner’s authorized representative, the ELS Contractor shall complete required correction of each outstanding item on the system adjustment list.  After all items appearing on the installation/inspection report are completed, the Owner's authorized representative will make an appropriate approval.